## Sheet1
GENERAL | 1 | Tag Number | [6 empty] | PCV-21002
| 2 | Service | [6 empty] | Purge DU-2101& D01 to LF
| 3 | P & ID Number |  |  | Line Number |  |  |  | 21-0-PR-0110 | [5 empty] | 1"-LF-2110002-AAC-N
| 4 | Line: |  | Material |  |  | Class |  | ASTM A106 GR.B,ASME B36.10 | [5 empty] | AAC
| 5 |  |  | Size/Schedule: |  | Inlet |  | Outlet | 1"/SCH 80 | [5 empty] | 1"/SCH80
| 6 | Allowable Sound Pressure Level (dBA) | [6 empty] | 85
| 7 | Tightness Requirement |  |  | Power Failure Position |  |  |  | NO | [5 empty] | NA
| 8 | Available Air Supply Pressure:(BARG) |  |  |  | Minimum |  | Maximum | 6.5 | [5 empty] | 7.5
| 9 | Function | [6 empty] | Back Pressure Regulator
PROCESS CONDITION | 10 | Process Fluid/State |  |  | Maximum Shut-off DP(BARA) |  |  |  | Nitrogen/ Vapor | [5 empty] | 3.5
| 11 | Ambient Temperature: |  |  | Operating | Minimum |  | Maximum | -3.5°C | [5 empty] | 52°C
| Process Specification: | [7 empty] | Unit |  |  | @ Minimum Flow |  |  | @ Normal Flow |  |  | @ Maximum Flow
| 12 | Flow Rate | [6 empty] | Kg/h |  |  | 9 |  |  | 10 |  |  | 11
| 13 | Inlet Pressure | [6 empty] | bara |  |  | 3.1 |  |  | 3.1 |  |  | 3.1
| 14 | Pressure Drop | [6 empty] | bar |  |  | 1.7 |  |  | 1.7 |  |  | 1.7
| 15 | Inlet Temperature | [6 empty] | °C |  |  | AMB. |  |  | AMB. |  |  | AMB.
| 16 | Molecular Mass | [9 empty] | 28.1 |  |  | 28.1 |  |  | 28.1
| 17 | Inlet Compressibility Factor | [6 empty] | ― |  |  | 0.999 |  |  | 0.999 |  |  | 0.999
| 18 | Inlet Viscosity | [6 empty] | cP |  |  | 0.02 |  |  | 0.02 |  |  | 0.02
| 19 | Inlet Specific Heats Ratio (Cp/Cv) |  |  | Base Temperature (°C) |  |  |  | ― |  |  | 1.40 |  |  | 1.40 |  |  | 1.40
| 20 | Set Point | [6 empty] | bara |  |  | 3.1 |  |  | 3.1 |  |  | 3.1
| 21 | Density / Specific Gravity(15.5°C) | [6 empty] | Kg/m3 |  |  | 3.18/ 0.99 |  |  | 3.18/ 0.99 |  |  | 3.18/ 0.99
| 22 | Design Pressure ( Bara) |  |  | Design Temprature( °C) |  |  |  | 4.5 | [5 empty] | 87
CALCULATION | 23 | Flow Coefficient CV | [6 empty] | - |  |  | 0.2 (*) |  |  | 0.22 (*) |  |  | 0.24 (*)
| 24 | Travel | [6 empty] | % |  |  | * |  |  | * |  |  | *
| 25 | SPL @ | [6 empty] | dBA |  |  | <50 (*) |  |  | <50 (*) |  |  | <50 (*)
BODY AND TRIM | 26 | Body Type |  |  |  | GLOBE |  |  | POSITIONER | 52
| 27 | Body Size | Trim Size |  |  | 1" (*) |  | * |  | 53 | Signal: |  | Inlet |  | Outlet |  | N/A |  | N/A
| 28 | Rated CV | Characteristic |  |  | * |  | Linear |  | 54 | Increase signal Valve | [5 empty] | N/A
| 29 | End Connection Type & Rating |  |  |  | Flanged,RF,300#,B16.5,Serated Finish |  |  |  | 55 | Cam Characteristic | [5 empty] | N/A
| 30 | Body Material |  |  |  | ASTM A105 |  |  |  | 56 | Bypass |  |  | Gauges |  |  | N/A |  | N/A
| 31 | Bonnet Type | Bonnet Material |  |  | STD |  | ASTM A105 |  | 57 | Electrical Connection |  |  | Process Connection |  |  | M20 ×1.5(ISO) |  | N/A
| 32 | Flow Direction |  |  |  | VTA |  |  |  | 58 | Manufacturer/Model | [5 empty] | N/A
| 33 | Flow Action To |  |  |  | OPEN |  |  | LIMIT SWITCHES | 59 | Type |  |  | Quantity |  |  | N/A |  | N/A
| 34 | Lubricator | Isolation Valve |  |  | N/A |  | N/A |  | 60 | Switch "1" Tag No. |  |  | Switch "2" Tag No. |  |  | N/A |  | N/A
| 35 | Guiding | No. of Ports |  |  | * |  | * |  | 61 | Switch "1" Contact Action | [5 empty] | N/A
| 36 | Trim Type |  |  |  | * |  |  |  | 62 | Switch "2" Contact Action | [5 empty] | N/A
| 37 | Rated Travel |  |  |  | * |  |  |  | 63 | Contacts Rating |  |  | Electrical Connection |  |  | N/A |  | N/A
| 38 | Plug / Ball / Disk Material |  |  |  | 316SST |  |  |  | 64 | Elec. "Ex" Protection |  |  | Ingress Protection |  |  | N/A |  | N/A
| 39 | Seat Material | Seat Leakage Class |  |  | 316SST |  | IV | SOLENOID VALVE | 65 | Tag Number | [5 empty] | N/A
| 40 | Cage | Stem Material |  |  | 316SST |  | 316SST |  | 66 | Body Material |  |  | Trim Material |  |  | N/A |  | N/A
| 41 | Gasket Material | Packing Material |  |  | VTA |  | GRAFOIL |  | 67 | No. of Ports |  |  | Mounting |  |  | N/A |  | N/A
| 42 | Nace |  |  |  | NO |  |  |  | 68 | Power Supply |  |  | Elec. Connection |  |  | N/A |  | N/A
| 43 | [8 empty] | 69 | Safety Execution |  |  | Ingress Protection |  |  | N/A |  | N/A
| 44 | Manufacturer/Model |  |  |  | * |  | * |  | 70 | Solenoid Energized Action | [5 empty] | N/A
ACTUATOR | 45 | Type (Note 1) |  |  |  | spring-opposed Diaphragm |  |  |  | 71 | Single/Double Coil |  |  | Reset |  |  | N/A |  | N/A
| 46 | Size | Area |  |  | * |  | * |  | 72 | Manufacturer/Model | [5 empty] | N/A
| 47 | Failure Valve | Bench Range |  |  | CLOSE |  | * | OPTIONS | 73 | Air Set: |  | Set Pressure
| 48 | Handwheel Location |  |  |  | NO |  |  |  | 74 |  |  | Filter/Regulator |  |  | Gauge | N/A |  | N/A
| 49 | [8 empty] | 75 | Air Volume Tank | [5 empty] | N/A |  | N/A
| 50 | [8 empty] | 76 | Hydrostatic Testing |  |  | Leakage Testing |  |  | Required |  | Required
| 51 | Manufacturer/Model |  |  |  | * |  |  |  | 77 | Certification | [5 empty] | EN-10204-3.1B
| 78 | Purchase Order Number |  |  |  | Will be filled later |  |  |  | 79 | Serial Number | [5 empty] | *
NOTES
Note 1: Actuator case and yoke shall be carbon steel casting.
3
3

## Sheet2
GENERAL | 1 | Tag Number | [6 empty] | XV-21001
| 2 | Service | [6 empty] | LIGHT END HC INLET TO D-2101
| 3 | P & ID Number |  |  | Line Number |  |  |  | 21-0-PR-0101 | [5 empty] | 6"-LTE-2101001-AAC -N
| 4 | Line: |  | Material |  |  | Class |  | ASTM A106 GR.B,ASME B36.10 , NACE,BE | [5 empty] | AAC
| 5 |  |  | Size/Schedule: |  | Inlet |  | Outlet | 6" |  |  | SCH.40 |  |  | 6" |  |  | SCH.40
| 6 | Allowable Sound Pressure Level (dBA) | [6 empty] | <85 dbA
| 7 | Hazardous Area Classification | [6 empty] | Zone II, Gas Group IIC, T4
| 8 | Available Air Supply Pressure: |  |  |  | Minimum |  | Maximum | 6.5 BARG | [5 empty] | 7.5 BARG
PROCESS CONDITION | 9 | Fluid |  |  | State |  |  |  | LIGHT END HC | [5 empty] | L
| 10 | Flow Rate:(Kg/h) |  | Minimum |  | Operating |  | Maximum | 17600 |  |  |  | 44000 |  |  |  | 48400
| 11 | Pressure (barg): |  | Operating |  |  | Design |  | 10 | [5 empty] | 15.5
| 12 | Temperature (°C): |  | Operating |  |  | Design |  | 45 | [5 empty] | 87
| 13 | Maximum Differential Pressure for Actuator Size(bar) | [6 empty] | 15.5
| 14 | Viscosity (cP) @ Oper. Condition |  |  | Molecular Mass |  |  |  | 0.171~0.177 | [5 empty] | 70.04
15
16
BODY AND TRIM | 17 | Body Type |  |  |  | Floating Ball/Top Entry |  |  | LIMIT SWITCHES | 43 | Type |  |  | Quantity |  |  | Proximity |  | 2
| 18 | Body Size | Body and Bonnet Material |  |  | 6" |  | ASTM A216 WCB |  | 44 | Switch "1" Tag No. |  |  | Switch "2" Tag No. |  |  | ZSO-21001 |  | ZSC-21001
| 19 | Body Form |  |  |  | Fire Safe-Note 4 |  |  |  | 45 | Switch "1" Contact Action | [5 empty] | Open
| 20 | Bore Type | Bonnet Type |  |  | Full Bore |  | STD |  | 46 | Switch "2" Contact Action | [5 empty] | Close
| 21 | Bore Size | Trim Material |  |  | 6" |  | 316SS |  | 47 | Contacts Rating |  |  | Electrical Connection |  |  | 1Amp@24Vdc |  | M20*1.5
| 22 | Guiding | No. of Ports |  |  | Top |  | Single |  | 48 | Safety Execution |  |  | Ingress Protection |  |  | Eex-i |  | IP-65
| 23 | Connections | Rating |  |  | Flanged |  | 300# |  | 49
| 24 | Flange Finish |  |  |  | RF,Serrated Finish,ASME B16.5 |  |  |  | 50
| 25 | Lubrication | Isolation |  |  | N/A |  | N/A | SOLENOID VALVE | 51 | Tag Number | [5 empty] | XY-21001
| 26 | Packing |  |  |  | Graphoil |  |  |  | 52 | Body Material |  |  | Trim Material |  |  | 316SS |  | 316SS
| 27 | Bolting |  |  |  | VTA |  |  |  | 53 | No. of Ports |  |  | Mounting |  |  | 3Way |  | Mounted(1)
| 28 | Leakage Class |  |  |  | Class VI |  |  |  | 54 | Power Supply |  |  | Elec. Connection |  |  | 24Vdc |  | M20*1.5(2)
| 29 | [8 empty] | 55 | Elec. "Ex" Protection |  |  | Ingress Protection |  |  | Eex-i |  | IP-65
| 30 | Maximum Shut-off DP. |  |  |  | 15.5 |  |  |  | 56 | Solenoid Energized Action | [5 empty] | Supply air to Valve
| 31 | [8 empty] | 57 | Single/Double Coil |  |  | Reset & Latch |  |  | Single |  | Yes
| 32 | [8 empty] | 58 | Reset Push Button | [5 empty] | No
| 33 | Rated CV |  |  |  | VTA |  |  |  | 59
| 34 | SPL @ dBA (Min./Nor./Max.) |  |  |  | VTA |  |  |  | 60 | Manufacturer/Model
| 35 | Nace |  |  |  | No |  |  | OPTIONS | 61 | Air Set: |  | Set Pressure |  |  |  | VTA
| 36 | Manufacturer/Model | [7 empty] | 62 |  |  | Filter/Regulator |  |  | Gauge | Required |  | Required
ACTUATOR | 37 | Type |  |  |  | Spring Return Piston, Pneumatic |  |  |  | 63 | Air Volume Tank | [5 empty] | N/A
| 38 | Size | Stroking Time |  |  | VTA |  | As per Specification |  | 64 | Hydrostatic Testing |  |  | Leakage Testing |  |  | Required |  | Required
| 39 | Orientation | Form |  |  | Vertical |  | Top Mounted |  | 65 | Certification | [5 empty] | Required(EN-10204-3.1.B)
| 40 | Air Failure Valve |  |  |  | Close |  |  |  | 66 | Handwheel | [5 empty] | YES-Lock Close-Side Mounted
| 41 | Air Supply Connection |  |  |  | 1/4" API X 1/4" OD-Screwed Compression Type |  |  |  | 67 | Mechanical Position Indicator Device | [5 empty] | Required With 2 Position of Valves
| 42 | Manufacturer/Model | [7 empty] | 68 | Tube and fitting | [5 empty] | 316SS ,1/4" OD NPT
| 69 | Purchase Order Number | [7 empty] | 70 | Serial Number
NOTES | 1)The Soleniod valves shall be mounted and tubed by the ON/OFF valve vendor.The solenoid valve size &type , Tubing Size, The actuator air connection Size and the air filter regulator capacity shall be determined by the ON/OFF valves Vendor to meet the maximum stroking time requirement specified for the ON/OFF valves
2)Connection of cable shall be completed with terminal blocks, Ground terminal clamping the cable armouring
3)Deleted
4)All ball valves shall be fire safe construction , anti static device , anti blow out stem .
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
4
4